## Sheet1
Manufacturer | Type | Capacity | Alarm Code | Alarm text | Description | Suggestion | Description of Action | Parts | Tool | PPE | Down time / Working | Engineer | Result(Y/N) | Issues | Remark | Date | Site | WT No.
01 | 01 | 02 | 0 | Turbine OK | If the error the turbine has stopped with has reset before the turbine has delivered the alarm call to the QSL server, this error can occur. Can also occur on yaw errors |  |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 1 | Illegal InitVal data in PROM | Internal system error. | Reboot the controller. Upload new software. Upload parameters whit parameter wizard
|  |  | 2 | Conflict: Rack/Turbinetype | Internal system error. The rack does not match the selected turbine type. | Reboot the controller. Upload new software. Upload parameters whit parameter wizard
|  |  | 3 | Ground CT____ missing (pos.__) | A CT module is defekt or missing. | Check the CT module for a bad connection. Change the CT module |  |  | 1. Multimeter | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 4 | Top CT____ missing (pos.__) | The turbine may be restarted once. If the turbine breaks down right after start up, servicefitter must be dispatched, to the turbine. Make notification. | Check comunication to top rack. Check CT module in top rack. |  |  | 1. Multimeter | 1. Helmet
|  |  | 5 | Wrong ARCNet node no. | Internal system error. | Check DIP switch settings in COM module, if settings are correct change module. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 6 | Serial communication not init. | Internal system error… | Reboot the controller. Upload new software. Upload parameters whit parameter wizard. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 7 | CT3218 initialization error | CT3503 can't start communnication with CT3218. This error is often seen if the software in CT3218 is too old. | If possible upload new software. Check the version on the CT 3218 if it is a 01 change it to a CT 3218.02 The error can allso accure when CT3203 is defekt. |  |  | 1. Multimeter 2. Spanner 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 8 | CT3220 initial. error pos.__ | CT3503 can't start communication with CT3220. This error is often seen if the CT3220 is defect, or is configured with the wrong type of piggybacks. E.g. FFFF instead of BF. | Check the CT3220 and piggy back settings. |  |  | 1. Multimeter | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 9 | Initialisation of ArcNet | Internal system error. |  |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 10 | CT3232 initialization error | CT3503 can't start communication with CT3232. This error is often caused by a defect, or missing module. | Check CT module 3232. Check software. |  |  | 1. Multimeter 2. Spanner 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 11 | Unexpected interrupt | Internal system error. | Reboot the controller. Upload new software. Upload parameters whit parameter wizard.
|  |  | 12 | Too many digital filters | nternal system error. | Reboot the controller. Upload new software. Upload parameters whit parameter wizard.
|  |  | 13 | Too many sublogics | Internal system error. | Reboot the controller. Upload new software. Upload parameters whit parameter wizard.
|  |  | 20 | Too many event timers | [5 empty] | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 24 | Event timer not initialized | [5 empty] | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 27 | Illegal text no.:______,__ | Internal system error in the controller. | Upload new software and check bulletin for new software. Remember to take ramdump if possible. Use parameter Wizard to upload parameters. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 30 | Internal sublogic error | Internal system error. upload new soft ware. | Check battery in controller and upload new software. upload parameters whit parameter Wizard. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 33 | TelegramRcv resource too small | The error is generated, if one of the processores (Top, ground, Grid, etc.) has received more data than it can process. | Check battery in controller and then Reboot the Controller. Check processors. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 36 | No communication with Top | The ground processor has lost contact with the top processor, after the communication to the top has been established. The ArcNet hardware may be unstable, or the top processor has stoppede responding due to an error in the top processor. If the error is seen every time the turbine does a specific thing, example. pause mode; connecting to the generator, the changed paramerers should be checked, recording to the latest parameter list. Check software version. | Check CT 3514 in top and ground./ Fiber line from top to ground. / The error can also be in the rack, powersupply, or the CT3513. Check the switch settings in 3514. (V66: CT3513). |  |  | 1. Multimeter 2. Spanner 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 38 | No comm. with ComController | The ground processor has lost contact with the communication processor, after the communication to the com.controller has been established. The ArcNet hardware may be unstable, or the com. processor has stopped responding due to en error in the com. processor. | The reason can be in hardware, specially CT3514 in nacelle and com.ctrl., and the fibre, but the reason can also be in the rack, powersupply, or the CT3251. Check switch settings in CT3514. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 40 | SW versionconflict GND/COM | The software in the Ground and Communication controller, doesn't match. This indicates that software has not been uploaded to all computers during upload. | Upload new software. upload parameters whit parameter Wizard. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 44 | SW versionconflict GND/TOP | The software in the Ground and Top controller doesn't match. This indicates that software has not been uploaded to all computers during upload. | Upload new software. upload parameters whit parameter Wizard. |  |  | 1. Multimeter 2. Spanner 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 45 | SW versionconflict GND/GRID | The software in the ground and grid processor doesn´t match. This indicates that software has not been uploaded to all computers during upload. | Upload new software. upload parameters whit parameter Wizard. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 47 | CT 3218 data error _,__ | The error is generated, if the CT3503 modul receives data in a wrong format from the CT3218 modul. This error is offen seen if the software in CT3218 is too old. If the CT3218 is a version 01, then CT3503 can´t update the software in CT3218 | Check if the CT3218 is defekt. Check the version number on CT3218 it needs to be at least version 02. Check CT3503. Upload new software. Upload parameters whit parameter Wizard. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 48 | Too many ArcNet retransmiss. | The processors looses data when communicating, and is retransmitting data to often. This error is a indication af an electrical or optical problem in the arcnet. | The fault can be in the CT3514/CT3513, The rack, CT3251, or the rotating arcnet interface (V63/V66) |  |  | 1. Multimeter 2. Spanner 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 49 | Too many ArcNet reconf._____ | The Arcnet has been reconfigured (restarted) 10 times this day. During a reconfiguration there is an communication blackout lasting up to 1 sec. | Check connection/communication between Ground, Nacelle, Hub, VCP board and CT291 integrated terminal in ground controller. Check dip switch settings “inside” Top processor CT3514 “Inside” Hub processor CT3514 “Inside” Ground processor CT 3514 And VCP Board CT294. Check the version of the processor. If the processor has been changed it’s important to verify that they are a version 3. Do to version 1 and 2 will not communicate with each other. Check rotating transfer/contact. If all the things are correct, try to Upload new soft ware whit parameter wizard. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 52 | ZeroCross interrupt missing _ | The power controller CT3251 is not receiving stable zerocross interrupte, and the controller is not able to measure voltage, current, frequency and power correct. CT3251 is receiving the interrups from s separate transformer in CT206/CT227. If the message has a "0" in the text, the interrups has been missing for 2 grid periods. This error can occur if the voltage suddenly drops, or due to fluctuations from faults somewhere in the grid. If the message has a "1" in the text, the interrups is too frequent. This fault is also seen if the grid has high frequency noise, or the PFC discharge chokes is defect. | Check; CT206/CT227. / CT3251. / Check the cable connection Between CT3251 and CT206/CT227...... (CT228)
|  |  | 56 | Telegram lost during xmission | System error in the VMP (Vestas Multi Control) Controller. | Check connection/communication between Ground, Nacelle, Hub, VCP board and CT291 integrated terminal in ground controller. Check dip switch settings “inside” Top processor CT3514 “Inside” Hub processor CT3514 “Inside” Ground processor CT 3514 And VCP Board CT294. Check the version of the processor. If the processor has been changed it’s important to verify that they are a version 3. Do to version 1 and 2 will not communicate with each other. Check rotating transfer/contact. Reboot controller. If all the things are correct, try to Upload new soft ware whit parameter wizard. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 62 | Ground status report timeout | System error in the control, the ground controller has missed the report telegram from the top controller. | Check connection/communication between Ground, Nacelle and CT291 integrated terminal in ground controller. Check dip switch settings “inside” Top processor CT3514 and “Inside” Ground processor CT 3514. Check the version of the processor. If the processor has been changed it’s important to verify that they are a version 3. Do to version 1 and 2 will not communicate with each other. Reboot controller. If all the things are correct, try to Upload new soft ware whit parameter wizard.
|  |  | 63 | Power telegraph timeout | System error in the VMP (Vestas Multi Control) Controller. | Check CT3251 in ground controller also check the in and out put signal to this processor. Check The 5 VDC supply from CT 3357 to CT3251. Reboot controller. Check the version of the CT processors, if it's a version 01. change them whit a new version. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 68 | HV Trafo. vent. _, temp:___°C | HV Trafo. vent. _, temp:___°C criteria : Logged when the RCC fan are starting and stopping. The fan starts at 130°C (P6.10) and stops at a temperature 30°C (P6.11) below the start limit |  |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 71 | Feedback=_, Int. Gen.Fan S___A | The feedback from the internal generator ventilators is not correct in 10 sec. | Check Feedback S513A and Feedback S515A. Check contact K513A and K515A. Check CT3153 pos Y3. Check CT3133 pos X3. Link to document: V63 and V66 AI: 943815. AI: 943816 and AI:943772 Drawing 924271. Drawing 924275 Drawing 924234 Drawing 924235. V80 1,8 AI: 947839 AI: 947842 and AI: 947849 Drawing 929204 Drawing 929205 and Drawing 929207. |  |  | 1. Multimeter 2. Spanner 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 72 | Feedback=_, Int. Gen.Fan S___B | The feedback from the internal generator ventilators is not correct in 10 sec. | Check Feedback S513B and Feedback S515B. Check contact K513B and K515B. Check CT3153 pos Y3. Check CT3133 pos X5. Link to document: V63 and V66 AI: 943815. AI: 943816 and AI:943772 Drawing 924271. Drawing 924275 Drawing 924234 Drawing 924235. V80 1,8 AI: 947839 AI: 947842 and AI: 947849 Drawing 929204 Drawing 929205 and Drawing 929207. |  |  | 1. Multimeter 2. Spanner 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 73 | Feedback=_, Ext. Gen.Fan S___ | The feedback from the external generator ventilator is not correct in 10 sec. | Check Feedback S507 and Feedback S509. Check Contact K507 and K509 Check CT3153 pos Y3 top controller. Check CT3133 pos X3 top controller. Check all connections in this circuit. Links to document: V63 and V66 AI: 943815 AI: 943816 and AI: 943772 Drawing 924234 and Drawing 924235. V80 1,8 AI: 947842 AI:947839 AI:947849 Drawing 929204 and Drawing 929205. |  |  | 1. Multimeter 2. Spanner 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 76 | Low processor temp. Comm Ctrl. | The temperature has dropped bellow the controllers specified temperature limit 0°C "S304". The turbine is put in pause mode by the controller, before the power supply is cut off. The reason can be a fault in the heating element, or the PTS5 temp. sensor. | The reason can be a misadjusted thermostat, an fault in PTS5 temp sensor. heating element, or the door is not closed. Check adjustment of thermostal B304. Test the PTS5, check the heating element. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 77 | Low processor temp. in Nacelle | This error is generated, if the temperature in the nacelle comes below the temp. limit, that is allowed in that turbine type. When the temp. reach the right setpoint the turbine will auto reset. But only if the temp. sensor in the nacelle not is broken. If the temp. sensor in the nacelle shows -205 or +205 deg. the sensor is broken, and need to be replaced before the turbine can run again. | Check S305. Check B305A, B305B and D305A. Check PT100 R306. Check setting of thermostat in Nacelle controller and VRCC controller. Check CT3133 pos X6 Check CT3220 PosX7 Check connections in this circuit. Links to document: V63 and V66 AI: 943815 AI: 943816 and AI: 943772 Drawing 924238 and Drawing 924239. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 78 | Low processor temp. in Hub | The temperature has dropped bellow the controllers specified temperature limit 0°C "S304". The turbine is put in pause mode by the controller, before the power supply is cut off to the hub controller. The reason can be a misadjusted thermostat, an fault in PTS5 temp sensor. heating element, or the door is not closed. | Check B304A, B304B and D304A Test the PTS5, check setting of thermostat and the function of the heating element. |  |  | 1. Multimeter 2. Driver 3. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 79 | PFC breaker open | The error is reported, if the circuit breaker PFC Q7 for the phasecompensation is open, and the turbine can´t connect to the grid. This error normal occures after service visit, if the service crew not have connected the Q7 breaker. | Check / Close the circuit breaker Q7. |  |  | 1. Multimeter 2. Driver 3. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 80 | Low gear oil pressure | The gear oil system cannot maintain the necessary pressure. The error can occure if the pressostat "S412" is misadjusted, or if the mechanical gear oil pump not can provide the right pressure in the gear oil system. | Check that the gearoil pumpe can provide oil when the gear rotating with 300 rpm. If not.! check the drive in the mechanical gearoil pump not is broken. Some mechanical gearoil pumps is mounted with wire dowel, check if this is broken. Check if the pipes to the gearoil pump is tightent right, and the suction pipe not is blocked by metal shaving, from e.g. a damage gear. If this is ok, then check the oil pressure on pos. 5, with a rotation on 1500 rpm." Direckt pressure from the gearoil pump." The pressure has to be between 2-5 bar, depending on the temp. and the gear type. When this is ok, check the pressure on pos. 12 "Pressure after the gearoil filter and where the pressostat S412 messure the pressure" If the pressure is under 1,0 bar, messured on pos. 12. can it be a error in a 3,5 bars overpressure valve. This can cause the gearoil pressure disappearing, and not lubricate the bearings. Normal this is happing on the small valveblocks "HC 35 filters". suggestion: If all the purssure is ok, check the pressostat S412 with VT 742124 and a 0-10 bars manometer. The S412 has to switch off by the pressure 0,5 bar ± 0,1 bar, with dropping pressure. If S412 is broken, change the pressostat S412, and adjust the new one to 0,5 bar. Check the signal S412 changing from + to - in picture 14D. |  |  | 1. Thermometer 2. Spanner 3. Driver 4. Multimeter | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 81 | Pitch B ref:__._°, Act.:__._° | The difference between pitch and the actual pitch has been higher than the allowable limit. | Check; The plug connection to proportional valve Y800B. pos.82./ Defect proportional valve Y800B pos.82. Item no. 193415. / High friction in bearing… |  |  | 1. Thermometer 2. Spanner 3. Driver 4. Multimeter | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 82 | Pitch C ref:__._°, Act.:__._° | The difference between pitch and the actual pitch has been higher than the allowable limit. | Check the plug connection to proportional valve Y800C. pos.82./ Defect proportional valve Y800C. pos.82. Item no. 193415. / High friction in bearing.
|  |  | 83 | B Ctrl:___.__V P.Vel:___._°/s | The difference between expected pitch velocity and the actual pitch velocity has been higher than the allowable deviation. | Check for bad connections to the proportional valve. / Defect porportional valve. / High friction in pitch baring. |  |  | 1. Spanner 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 84 | C Ctrl:___.__V P.Vel:___._°/s | The difference between expected pitch velocity and the actual pitch velocity has been higher than the allowable deviation. | Check for bad connections to the proportional valve. / Defect porportional valve. / High friction in pitch baring. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 85 | B CtrlV.STD _.___V MEAN__.___V | The error is reported, if the standard deviation on the control voltage to the proportional valve is higher than 7 volt for the last 10 sec. | Possible reasons : -fault in position tranducer (Balluf), -Controller is unstable., -Fault in (V)RCC (on turbines with RCC) |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 86 | C CtrlV.STD _.___V MEAN__.___V | The error is reported, if the standard deviation on the control voltage to the proportional valve is higher than 7 volt for the last 10 sec. | Possible reasons : -fault in position tranducer (Balluf), -Controller is unstable., -Fault in (V)RCC (on turbines with RCC) |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 87 | Pitch dev. min:__._° max:__._° | The difference in pitch angle between the pitch system with the largest and smallest angle is greater than 12° deg. | Check signal A800A, A800B and A800C. Check the signal from the Balluf on each blade. Check each cable for Balluf. Check adjustment of Balluf. According to, service instruction AI: 943642. Check for loose connections in the circuit. Check CT3220 pos X2. Check 24V from CT3133 pos X1. Links to document: V80 1,8 AI: 947842 AI: 947839 and AI: 944915 Drawing 924216. V63 and V66 AI: 943815 AI: 943816 and AI: 943773 Drawing 924216. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 89 | Trip F60 L_: ___ °C |  |  |  |  | 1. Multimeter 2. Grip tool 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 91 | System error (2) | This error can happen due to a number of reasons, but it is offen due to errors in parameters in the pitch system. Offen it´s not possible to reset the turbine. | : Upload new software whit Parameter Wizard. |  |  | 1. Multimeter 2. Grip tool 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 100 | Too many auto-restarts:_____ | The turbine had exceeded its max limit of auto restarts, normal 10 auto-restarts. | Check Warning Log, check Alarm log and check system log. There will typical be a fault that is repeating. |  |  | 1. Multimeter 2. Grip tool 3. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 101 | Emerg.-> Stop, EMC not conn. | The Emergency circuit is not connected. The failure,occure when the turbine turns in emergency stop. | Check S902, S903, K900, K901, K903A, K903B, K906 and D906. Check out that the emergency buttons are released. Check CT3133 pos X6, CT3153 pos Y1 and CT3153 Y2. Check brake thermister. Check Battery backup. Check connections in the circuit. Links to document: V80 1,8 AI: 944919 AI: 947842 AI:947839 and AI: 947849 Drawing 929210, 929201 and 929203. V63 and V66 AI: 944919 AI: 943815 AI: 943816 and AI: 943772 V39-V47 AI: 941876 AI: 941877 AI: 941878 and AI: 941823 |  |  | 1. Multimeter 2. Grip tool 3. Driver 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 102 | Emergency circuit open | The turbine have an error and turned in to emergency stop. | Check S902, S903, K900, K901, K903A, K903B, K906 and D906. Check out that the emergency buttons are released. Check CT3133 pos X6, CT3153 pos Y1 and CT3153 Y2. Check brake thermister. Check Battery backup. Check connections in the circuit. Links to document: V80 1,8 AI: 944919 AI: 947842 AI:947839 and AI: 947849 Drawing 929210, 929201 and 929203. V63 and V66 AI: 944919 AI: 943815 AI: 943816 and AI: 943772 V39-V47 AI: 941876 AI: 941877 AI: 941878 and AI: 941823 |  |  | 1. Multimeter 2. Grip tool 3. Driver 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 103 | PhaseSequence error | This error is generated if the phase sequence on the grid is not correct. | check signal from A1, A2 and A3. Check CT206, CT227 and CT3251. Check VCP board CT294 and Link to document: V80 AI: 947849 and AI: 947848. V63 and V66 AI: 943772 V39-V47 AI: 941823 and AI: 941821. |  |  |  | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 104 | Phasesequence not measured | The VMP (Vestas Multi Control) CT3251 processor has not been able to meassure the phase sequence, perhabs because of very unstable grid frequency or voltage. | Check the fuse F34; Check CT206/227, and check CT3251. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 105 | Phase sequence check timed out
|  |  | 106 | Top OpSt.change timeout (_) | This is not an error this is an event it is when the SCADA and the turbine time is not the same and the SCADA is changsing the time in the turbine more then 5 Sec. |  |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 108 | Illegal gen.cmd.: _ in state _
|  |  | 110 | Feedback = _, Bypass contactor | The error is generated if the feedback from the bypassing is not correct in 10 sec. | On-site suggestion: Check Feedback S700A, S700B and S700C.Check CT3133 pos X1 and CT3153 pos Y1. Link to document: V39-V47 AI: 922509 AI: 922510 AI: 924786 AI: 946055 AI: 946065. V63 and V66 AI: 924231 AI: 924213 AI: 924205 and AI: 924237. V80 AI: 929201 AI: 927994 AI: 929207 And AI: 949191. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 111 | Feedback = _, Generator_ | The controller has not received an feedback signal from one of the generator contactors K500, K501, K502 in more that 10 sec. | Check the Feedback S500, S501 and S502. Check contactors K500, K501 and K502. Check that the contactor isn’t welded together. Check CT3133 pos X5 and CT 3153 pos Y1. On a V63, V66 and V80 check K700A-C and S700A-C. Link to document: V39-V47 AI: 924740 AI: 924879 AI: 924739 and AI: 946065. V63 and V66 AI: 924231 AI: 924213 AI: 924205 and AI: 924237. V80 AI: 929201 AI: 927994 AI: 929207 and AI: 949191. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 112 | Generatorbreaker open | Generator breaker is disconnected in the RUN state. This supervision prevents the turbine from being left with the breaker open after service visit. | Check Dip switch settings on the Q8. Check S8. Check CT3133 pos X1. Link to document: V39-V47 AI: 922510 AI: 924786 and AI: 946058. V63 and V66 AI: 924209 AI: 924205 and AI: 924237. V80 AI: 929203 AI: 927995 AI: 929207 and AI: 946193. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 113 | Bypass miss. before phasecomp_ |  | check the bypass K700 chech the signal from CT3153 to D700 and from D700 to K700 then check feedback from K700 |  |  | 1. Multimeter 2. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 114 | Feedback = _, Phasecomp__ | The feedback from phasecompenstion are not correct in 1000 msec.The error will be loged in the "Error Log list" Picture 9. If the log error says 0 = The turbine will proceed in run mode. If the log error says 1 = The controller will trip CB Q8. and stop the turbine "Emergency" Feedback from contactors: Feedback 1. means that feedback is activ but no signal has been given to the contactor. Feedback 0. means that feedback is not active even though a signal has been given to the contactor. | On V39 to V47 turbine Check Feedback S601, S602, S603 and S604. Check contactors K601, K602, K603 and K603. Check CT3133 pos X1 and CT 3153 pos Y1. On V63 and V66 Check S651, S652, S653, S654, S655, S656, S657, S658, S659, S660 and S661. Check contactors K651, K652, K653, K654, K655, K656, K657, K658, K659, K660 and K661. Check CT 3133 pos X1 and CT 3153 pos Y1. On V80 Check S651, S652, S653, S654, S655, S656, S657, S658, S659, S660, S661 and S662. Check contactors K651, K652, K653, K654, K655, K656, K657, K658, K659, K660, K661 and K662. Check CT 3133 pos X2 and CT 3153 pos Y1. Link to document: V39-V47 AI: 922510 AI: 924786 AI: 946055 and AI: 946065. V63 and V66 AI: 924210 and 924232. V80 AI: 927993 AI: 929202 AI: 946191 and AI: 927994. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 117 | Anemom.error:__._m/s,____._RPM | This error can be due to an defect, or an iced anemometer. When the generator speed exceeds 90 percent of nominal speed it is checked, that the anemometer shows at least 0.1 m/s. | Check Anemometer B301. B301B if tower anemometer is installed (option) ; / Check the communitions cable W381. W381B if tower anemometer is installed (option). Check CT3218. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 118 | Anemom.error:__._m/s,____._kW | This error occure if the difference between the meaured power and the measured wind has to high deviation from the powercurve. The error occurs during cold weather, where there is a chance of over-iceing, or if the sensor is defekt | Check Anemometer B301. B301B if tower anemometer is installed (option) ; / Check the communitions cable W381. W381B if tower anemometer is installed (option). Check CT3218. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 119 | Extrem frequency: ___.__ Hz | The turbine has discovered a frequency error on the grid, which has turned the turbine in to emergency stop. | Check A1, A2 and A3. Check CT3251 pos Z2. Check capacitor circuit system V39: exchange CT`s 3305 and 1124 (power supply) |  |  | 1. Multimeter 2. Thermometer 3. Grip tools 4. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. insulation Gloves
|  |  | 120 | Low curr.L1:____A,Others:____A | The error is generated, if the grid current in one phase, deviate more than 7,5% in one 1 second, from the other phases. | Check A4, A5 and A6 Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 121 | Low curr.L2:____A,Others:____A | The error is generated, if the grid current in one phase, deviate more than 7,5% in one 1 second, from the other phases. | Check A4, A5 and A6 Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 122 | Low curr.L3:____A,Others:____A | The error is generated, if the grid current in one phase, deviate more than 7,5% in one 1 second, from the other phases. | Check A4, A5 and A6 Check CT3251 pos Z2. Check capacitor circuit system Check CT318. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 123 | High curr Gen0 L_: ____ A | The error is generated, if the generator has a high current over 13% of the nominal current in 1,6 sec. | Check A4, A5 and A6 Check CT3251 pos Z2. Check capacitor circuit system There are vdf-track examples for this error in the linked xls-file(s). |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 124 | Extr.high curr.Gen1 L_: ____ A | The current in a phase has been over 5% or under 5% of nominal current in 10 sec. | Check A4, A5 and A6 Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 125 | Extr.high curr.Gen2 L_: ____ A | The current in a phase has been over 5% or under 5% of nominal current in 10 sec. | Check A4, A5 and A6 Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 126 | Extr. high volt. L_: ___ V | The error is reported, if the voltage in a phase has been over the limit, for nominal voltage in 200 msec. | Check A4, A5 and A6 Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 127 | Extr. low voltage L_: ___V | The voltage in a phase has been under nominal voltage. Reason could be an error in the grid connection. | Check A4, A5 and A6 Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 128 | Trip Q8 L_: ___ V | The error is reported, if the voltage has been 20% over nominal voltage in 80 msec. The controller can trip CB Q8 due to : -Overvoltage; -Overcurrent; -Feedback error, or welded contactor. | If the turbine has tripped CB Q8, the grid voltage has to be checked before the breackers is closed, and controller is started. When the controller is started, it can be seen in the log why the conrtoller has tripped Q8. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 129 | Frequency error: ___.__ Hz | The frequency has been over or under the permitted setpoint limit for more than 200 msec. This error occure if there is a frequency error on the grid. | Check A1, A2 and A3. Check CT3251 pos Z2. Check capacitor circuit system V39: exchange CT`s 3305 and 1124 (power supply) |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 130 | Max power Gen_: ____._ kW | The measured power has been higher than the limit of nominal power setpoint. | Check A1, A2, A3, A4, A5 and A6. Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. insulation Gloves
|  |  | 131 | Negative power Gen_: ____._ kW | The error is reported, if the measured power has been below 50% of the nominal power. | Check A1, A2, A3, A4, A5 and A6. Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. insulation Gloves
|  |  | 132 | Leak current ____A | There has been a leak current to ground. | Check A4, A5 and A6 Check CT3251 pos Z2. Carry out a thyristor test. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. insulation Gloves
|  |  | 133 | Power: ____._ kW, OpSt |  | Check the pitch sys. do all the picth test in menu 11
|  |  | 134 | High voltage L_: ___ V | The voltage in one of the phases has been over the nominal limit voltage in 60 second | Check A1, A2 and A3. Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 135 | Low voltage L_: ___ V | The voltage in a phase has been under nominal voltage in 60 seconds. Normal this error can occure if the grid is cut off. | Check A1, A2 and A3. Check CT3251 pos Z2. Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 136 | Asym.currL1:____A,Others:____A | The current is not symmetric on the three phases. The asymmetrical current has for more than 10 sec. been over the limit. The supervision is activated when the current is lager than 30% off the nominal current. The reason can be a fault in the turbine, or the grid where many consumers are on the same phase somewhere in the grid. | Check the VCS-true card; check the VCP board CT318. (V47-V66 (V)RCC Check if the PFC batteries is drawing the same current on all phases.) |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 137 | Asym.currL2:____A,Others:____A | The current is not symmetric on the three phases. The asymmetrical current has for more than 10 sec. been over the limit. The supervision is activated when the current is lager than 30% off the nominal current. The raeson can be a fault in the turbine, or the grid where many consumers are on the same phase somewhere in the grid. | Check the VCS-true card; check the VCP board CT318. (V47-V66 (V)RCC Check if the PFC batteries is drawing the same current on all phases.) |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 138 | Asym.currL3:____A,Others:____A | The current is not symmetric on the three phases. The asymmetrical current has for more than 10 sec. been over the limit. The supervision is activated when the current is lager than 30% off the nominal current. The raeson can be a fault in the turbine, or the grid where many consumers are on the same phase somewhere in the grid. | Check the VCS-true card; check the VCP board CT318. (V47-V66 (V)RCC Check if the PFC batteries is drawing the same current on all phases.) |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 139 | Asym.voltL1:____V,Others:____V | The grid voltage is asymetric. | Consider the reasons may be that there are several consumers on one single phase on the grid. Check the phases on each side of the Q8. Check signal from A1, A2 and A3 and Check TRU card and the 5,5 V on VCP board.If necessary change VCP board. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 142 | High curr Gen1 L_: ____ A | The current in a phase has been 13% over nominal current for the connected generator, without/with capacitors connected for more than 20 sec. | check A4, A5 and A6. Check CT3251 pos Z2 Check capacitor circuit system |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 143 | High curr Gen2 L_: ____ A | The current in a phase has been 13% over nominal current for the connected generator, without/with capacitors connected for more than 20 sec. | check A4, A5 and A6. Check CT3251 pos Z2 Check capacitor circuit system. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 144 | High windspeed: __._ m/s | The vindspeed averaged over 25 seconds has been measured to high to allow the turbine to keep running. This is under normal circumstances a normal error, and the turbine will autoreset when the windspeed dropping. | This error is generated do to high wind. There might be a defekt in anemometer or US sensor |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 145 | Low processor temp. in top | The temperature has dropped bellow the controllers specified temperature limit 0°C "S304". The turbine is put in pause mode by the controller, before the power supply is cut off to the top controller. The reason can be a misadjusted thermostat, an fault in PTS5 temp sensor. heating element, or the door is not closed. | Check adjustment of thermostal B304. Test the PTS5, check the heating element. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 146 | Ambient temperature low: ___°C | The ambient temperature is lower than -20° deg. in 60 sec. | Check; Ambient sensor R300; / Check cable connection W380 from sensor to the connections box A9. (con. Ø10, Ø11.) (V66); / Check cable connection W384 from connections box A9 to CT3220.(V66): / Check cable connection W380 from sensor to CT3220. (V47). |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 147 | High gear temperature:____°C | The temperature in the gearbox is higher than the permitted setpoint limit temp | Check parameter. Picture 24.5 ”Transmission” . (” ºC Max gear temp limit “) : (“ ºC Max gear temp hyst”) : (" sec Max gear temp. timeout") Check parameter recording to the latest parameter list. Check the electrical cooler pump is working and there is coming oil trough the system when the turnine is running. (if there are no oil coming when the turbine is running with the pump in on mode, then check the oil level in the gearbox). Check that the fan / 3 fans are working properly and they are starting at the right temperature (see electrical manual. "Gear oil system"). Check the PT100 for loose connections and it´s measuring the right temperature. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 148 | High temperature Gen_: ___°C | The generator has a temperature sensor. If the temperature is higher than the set value, the turbine is stopped. | Note! Check the Nacelle fan. Picture 11 "test menu" Grup 25. Naceller Fan. 3 = Automode. Check the temp. sensors, in the generator. / Check the internal, and the external ventilator mode. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Thermometer | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 149 | High temperature T53: ___°C L_ | The temperature in one of the trafo. windings has been higher than 150 °C | It’s only on V63, V66 and V80 this error occur. Start Whit Comparing the temperature ambient temperature, nacelle temperature and the HV transformer temperature. Check that the latch under the transformer is open. Check that all fan’s are operating whit out any errors. Check that no parameter settings has been change do to temperature surveillance and no contacts or parameter for fan has been changed. Check the PT100 R17A, R17B, R17C, R18 and R19. Check CT3220 pos X8. |  |  | 1. Multimeter 2. Driver 3. Thermometer | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 150 | High temp. bearing _: ___°C | The temperature of the gear bearing has exceeded the max. limit temperature. "R406" | Check the temperature sensor R406. Check the internal magnet for metal shavings, check for abnormal noise from HSS bearing at 300 rpm. (damaged bearing is high frequent noise) Check the oil pressure on position 5 on the valve block at 1500 rpm. (direct pressure from the pump) it´s suppose to be between 1,6 bar and 2,5 bar when the oil temperature is between 45 and 55 degrees. Check that there is coming oil to cooler 1 when the temperature is 45 degrees and over that temperature, (hot pipe) Check the oil pressure on position 12 at 1500 rpm, if it comes under 1 bar (typical 0,6-0,8 bar )at the same temperature it is possible the 3,5 bars overpressure valve inside the valve block that is defective and then is required to change the valve block. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Thermometer | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 151 | High temp. Gen bearing _:___°C | The temperature of the generator bearing has exceeded the max. limit temperature (91ºC) Type: Turbine error WTG mode after error: Pause Acknowledge level: Remote | Check the temp. sensor for the generator bearing ; Check the generator bearing for noise, and try to grease the bearings. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Thermometer | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 153 | Max generator RPM: ____._ RPM | The error is reported, if the generator RPM is found higher than the limil of nominal generator RPM. This error is typical seen when a powerfull gust has brought the turbine in an overspeed situation. | V47) Check the high speed sensor B401. Check connection box A3. check cable connection W482, CT3218 pos X3. Check the high speed shaft for abnormal axial clearance, call the hotline for further details regarding the tolerance depending gearbox type. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Thermometer | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 154 | Max rotor RPM: __._ RPM | The error is seen, if the rotor RPM is higher than then limit of the nominal generator rpm / gear rotation in 200 msec. The reason can be a gust more powerful than the control system can handle, or a problem in the roror RPM proximity sensor B400. | Check the distance between the sensor B400 and the rotor locking disc. / Check the cable commection from the sensor to the CT moduls. See drawing below. If the problem still exists, replace the proximity sensor wiht itme no. 114257, " type with pull down resistor" |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Thermometer | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 155 | Max slip gen_, RPM: ____._ RPM | This error is seen if the gernerator has been rotating too fast in a period of 5 - 30 sec. due to gusts, where the control system failed to keep the speed withen the limit. | Check B401 generator sensor and cable for sensor. Check CT3218 pos X3. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Thermometer | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 156 | Chock sensor trigged:____._RPM | This alarm is caused by a signal from the vibration sensor and indicates the occurence of very strong vibrations. | Check S403 shock sensor. Check that the wind vane/US sensor is operation without errors. Check that the turbine is yawing the nacelle correct upwind. Check for vibration do to blade damage or other defect components. Check pitch system. If nothing is found, take a VDF track and analyse it. Be aware that on new software release, the turbine need to be running with above 200 RPM. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Thermometer | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 157 | Gen.RPM: ____._ RPM, OpSt | The generator RPM has exceeded the max limit, monitored in pause and stop mode. | Check B401 generator sensor and cable for sensor. Allso check for noise. Check CT3218 pos X3. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 158 | Rotor:__._RPM, Gen.:____._ RPM | The difference of the rotor RPM and the generator RPM, has exceed the max limit deviation on 15% in 2 sec. | Check the adjustment of B400 rotor sensor. Check B400 rotor sensor and cable. Check generator sensor B401. CT3218 pos X1. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 159 | External RPM guard | The turbine has had an overspeed on the rotor. the error occurs it the turbine reach a set limit for how many rotations it may take per minut. This error is typical seen when a powerfull gust has brought the turbine in an overspeed situation. | Check the adjustment of the rotor sensor for the VOG ( Vestas Overspeed Guard ) / Check the VOG sensor damage. / Check the Cable connection from the sensor. / Check CT 3153. Check warning log and alarm log this error can occur when there is a grid fault. | 1. External RPM guard error inspection 2. Yaw system inspection |  | 1. Filler gauge 2. Fliers 3. Spanner 4. Hand tool | 1. Harness 2. Lanyard 3. Helmet 4. Sleeve | 9 / 7.5 | 3 | Y | - | - | 2018.01.18 |  | 행원 / #14
|  |  | 160 | High temperature brake disc | The temperature of the brake has exceeded its max. limit. | Check for worn brake pads, check for abnormal axial clearance on the high speed shaft, check for air in the brake calipers and bleed air out if necessary, check for loose cable connections W289, Check the connection from the thermister too the connections box A8. If it still fails check for short-circuit in the 24 volt volts system because it is the first failure in the stack. Check battery backup in emergency system. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 161 | Max time hydr. pumping:___ sec | The hydr. pressure limit are not reached after 60 sec. The error can occure a broken hydr. pump that not can provide the wished pressure in the hydr. system. | Measure the pressure on pos 19.1.( V66), M1 .(V47) / Check the hydr system for leak´s. / Check the Hydr. pump. (new hydr. pump item no 103965 V63-V66) (new hydr. pump item no 109927 V47). Check hose from the hydraulic pump allso check Relif valve. On MW turbines check hoses and valves in hub. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 162 | Safety-pressostat brake | The error is logged, if the pressure switch "S202" which monitors the pressure in the brake system is disabled. This error occure if the pressure in the brake system is under the limit setpoint. | Check the pressure switch S202. pos 26.1 . / Check the pressure reducing valve. pos.24. Item no. 194308 (V47). Check pressure in Brake accumulator. |  |  | 1. Multimeter 2. Driver 3. Grip tools | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 163 | Low workingpressure: ___._ bar | The hydraulic workingpressure has been too low. The pressure has been less than the limit for more than 200 msec. The reason can be a fault in the hydraulic system, or the turbine has pitched excessive due to turbulent wind, or unsuitability in control system. | Check the Hydr. pump (pos 2. V66) (pos 5. V47), in the hydr. system. Item no. 103965(V66); 109927 (V47). / Check the pressure transmitter (pos 23. V66) (pos 12. V47). Item no. 109270. (V66) 109526. (V47) |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 164 | Press.drop hydr. filter ___°C | This is an warning. The pressure drop across the filter has disconnected the pressurestat S201 | Check hydraulic oil temperature. Check hydraulic pressure drop switch S201. Change hydraulic filter. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 165 | Low oil-level, hydraulic | The oil level in hydraulic tank has been under the minimum limit, the level switch has deactivated S200 in 2 seconds, which has turned the turbine in emergency mode. | Check the hydr. oil-level. / Check the level swicth S200. pos. 14 (V66) pos. 2 (V47) Item no 109090. / Check the cable connection W282 between S200 and (CT3133 pos X5.) (CT3218 pos X3). |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 166 | Thermoerror hydraulicmotor | The hydraulic motor has been overloaded, and the thermorelay has disabled the supply to the hydr. motor (M204). | Check hydr. motor (M204) for overload. / Check the thermorelay (F205). |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 167 | Hydr. temperature high: ___°C | The error occure if the temperature in the hydraulic oil system is higher than 65° in 20 second. | Check the temp sensor R206, and the cable connection W281. (V66) Check the hydr. ventilator M241, and the cable W293 . Check if The hydraulic pump is working or is having problems to maintain the right pressure, this can occurse high temperature in the hydr. system. | (Hydr. Temperature 66℃) 1. Fill the Hydr. Oil 2. Hydr. Pump sensor, W281 cable inspection | 1. Texaco Rando WM 32 LT : 4L | 1. Spanner 2. Piers 3. Driver 4. Hand tool | 1. Harness 2. Lanyard 3. Helmet 4. Sleeve | 9 / 5.8 | 3 | Y | - | - | 2018.03.06 | 001 | #15
[7 empty] | (Hydr. Temperature high) 1. Hydr. Oil leak inspection (Brake caliper, Pitch cylinder) 2. Hub, pitch rod |  | 1. Torque wrench 2. Spanner 3. Pliers 4. Hand tools | 1. Harness 2. Lanyard 3. Helmet 4. Sleeve | 6 / 5.5 | 2 | Y | - | - | 2018.06.19 | 001 | #15
|  |  | 169 | Thermoerror nacelle fan F___ | A thermorelay has detected an overloaded nacelle fan motor, and the motor has been stopped. | Check the Vent. motor M340, for overload; check thermorelay F308 "low speed". F314 "high speed". Check the signal connection from F308, and F314. to CT3133 pos._ X5. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 170 | Thermoerr. gearoil cooler F___
|  |  | 172 | Feedback = _,:Nacelle fan S___ | The error occure, if the feedback signal from the nacelle ventilator contactor is not correct within 10 sec. The error can occure if the contactor for the nacelle ventilator is defekt, or if there is a bad cable connection. | Check Feedback S307, S313 and S317. Check contactors K307, K313 and K317. On V39 and V47 turbines check CT3133 pos X5 and CT3153 pos Y1. On V63, V66 and V80 turbines check CT3133 pos X3 and CT3153 pos Y3. Link to document: V39-V47 AI: 922653 AI: 924739 and AI: 924736. V63 and V66 AI: 924207 AI: 924271 AI: 924235. V80 AI: 929205 AI: 929204 AI: 927991 AI: 946195 AI: 927979 and AI: 946195. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 173 | Feedback=_, Gearoilcooler S___ | this is not an error this is an event | check the signal fron the from the CT to the contakt and the feedback from the contakt to the CT |  |  | 1. Multimeter 2. Driver 3. Thermometer | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 174 | Feedback = _,:Hydraulicmotor | The feedback from the hydraulicmotor are not correct in 1000 msec.The error will be loged in the "Error Log list" Picture 9. If the log error says 0 = The turbine will proceed in run mode. If the log error says 1 = The controller will trip CB Q8. and stop the turbine "Emergency" Feedback from contactors: Feedback 1. means that feedback is activ but no signal has been given to the contactor. Feedback 0. means that feedback is not active even though a signal has been given to the contactor. | Check Feedback S204. Check contact K204. On V39-V47 Check CT3133 pos X2 and CT3153 pos Y1 On V63, V66 and V80 check CT3133 pos X3 and CT3153 pos Y3. Link to document: V39 AI: 922653 AI: 924736 and AI: 924737. V63 and V66 AI: 924206 AI: 924270 and AI: 924235. V80 AI: 929204 AI: 929205 AI: 927991 AI: 946193 and AI: 946199. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 175 | High temp. bus bar section | The error occure if the temperature in the bus bar section, is higher than the max temperature limit. | Check the thermistor S311.Check all ventilators in controller. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 176 | Max temperature thyristors | The temperature in one of the thyristores is to high, and the concerned thyristore has been disabled (S702). The error can occure if the current through the thyristore is to high, witch result in a high temp in the thyristore. | Check thermister S702. Check thyristorV710-V715. On V39- V47 Check CT3133 pos X1 and CT 3251 pos Z2. On V63, V66 and V80 check CT3133 pos X5 and CT3251 pos Z2. Link to document: AI: 929207. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 177 | Low processor temp. in ground | The temperature has dropped bellow the controllers specified temperature limit 0°C "S304". The turbine is put in pause mode by the controller, before the power supply is cut off to the ground controller. The reason can be a misadjusted thermostat, an fault in PTS5 temp sensor. heating element, or the door is not closed. | Check adjustment of thermostal B304. Test the PTS5, check the heating element. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 178 | Def. fuse, lightning prot.(S9) | One of the tree surge arrestors is damaged, and signal S9 is disabled. The lightning protection fuse´s function is to protect the controller from over current/voltage, that can occure from the grid, or from a lightning. | Check the lightning detective fuse And the signal from it. On V39-V47 Check CT3133 pos X1. On V63, V66 and V80 check CT3133 pos X5. Link to document: V39-V47 AI: 946060 and AI: 924780. V63 and V66 AI: 924205 and AI:924237. V80 AI: 929207. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 179 | Error, yawcontrol: _____ | The combination of signals from the yaw control indicates an error in the signals, or the turbine is over waying the cables. | Check the yaw control and the twisted cables. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 180 | No yawpulses _____, ____ s | The turbine has been yawing continuously in the same direction in 600 sec, without no yaw pulse from the yawcontrol."S105", this error will send the turbine into stop mode. | Check the puls switch S105; Check / adjust yaw-sensor remember to on twist.; Check communication cable to the yaw-sensor. | (No Yawpulses 30010, 900s) 1. Middle tower main cable twist inspction 2. Yaw teeth inspection | - | 1. Multimeter 2. Spanner 3. Torque wrench 4. Hand tools | 1. Harness 2. Lanyard 3. Helmet 4. Sleeve | 3 / 2.5 | 5 | Y | - | 1. Yaw teeth 3개 손상으로 인한 발전기 가동 정지 | 2018.01.30 | 001 | #13
[7 empty] | (No Yawpulses 30010, 900s) 1. Yaw teeth inspection |  | 1. Spanner 2. Piers 3. Driver 4. Hand tool | 1. Harness 2. Lanyard 3. Helmet 4. Sleeve | 9.5 / 9 | 3 | Y | - | 1. Yaw teeth 9개 손상으로 이식 외 복구 방법이 없다고 판단, 제작사가 아닌 이상 작업 불가 | 2018.02.22 | 001 | #13
|  |  | 181 | Feedback = _,:Yaw CW | This error is generated, if the turbine has been Yawing CW in 10 sec. with out feedback signal. | Check/adjust yaw-sensor remember to on twist. Check the switch S105 in the yaw control. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 182 | Feedback = _,:Yaw CCW | This error is generated, if the turbine has been Yawing CW in 10 sec. with out feedback signal. | Check/adjust yaw-sensor remember to on twist. Check the switch S105 in the yaw control. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 183 | Max autoyawtime ____ sec. | Automatic yawing done continues in same direction for more than 1000 seconds. If it is very cold there can be a chance of ove-iceing on the windvane, or the windvane could be broken. | Check the Windvane (A327; V66) (B302; V47) : Check/adjust yaw-sensor remember to on twist. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 185 | Outyawing too much, S___ activ | The turbine has been outyawing in one direction too long, and a switch in the yaw conrtol has been activated. | Check the yaw control, and check the cables, before the turbine is started up again. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 186 | Thermoerror yawmotor F___ | The error is logged, if one yawmotors has been overloaded, and the thermorelay has disconnected the power supply to the yawmotor, and sent a signal to the VMP (Vestas Multi Control) Controller whit, witch yawmotor that has been overloaded. | (V47) Check yawmotor, M140A, M140B. / Check thermorelay F106, F107. / Check the communications cable from the thermorelay to CT3133. pos X2. | (Thermoerror yawmotor F106) 1. F106, F107 Thermo relay 2. K100, K101 Magnetic contactor |  | 1. Torque wrench 2. Spanner 3. Pliers 4. Hand tools | 1. Harness 2. Lanyard 3. Helmet 4. Sleeve | 7 / 6.5 | 2 | Y | - | 1. F106 Thermo relay, K101 Magnetic contactor 불량, 명일 #9 에서 탈거후 교체 예정 | 2018.04.16 | 001 | #15
[7 empty] | (Thermoerror yawmotor F106) 1. F106 Thermo relay replacement 2. K101 Magnetic contactor replacement 3. Yaw motor replacement 4. Fill Yaw gear oil | 1. Omala : 2L 2. Optimol : 2ea 3. Yaw motor(수리품) : 1ea | 1. Torque wrench 2. Spanner 3. Pliers 4. Hand tools | 1. Harness 2. Lanyard 3. Helmet 4. Sleeve | 4 / 3.5 | 2 | Y | - | - | 2018.04.19 | 001 | #15
|  |  | 187 | External 24 V power supply | No power supply for hydraulic festhering valves. On the V63/V66 this signal is also used for supervision of pressure on emergency accumulators. | Bad connection in supply to valves. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 188 | External 24 V power supply eq. | The error is reported if there is no power supply for proportional valve. | (V47) check the power supply T231, Fuse F83D "T.4amp.", signal S804 from K804. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 189 | Feedback = _, Brake | Error in the feedback connection from the brake. Feedback =. 0 = negativ feedback error. 1 = positiv feedback error. | Check the feedback S208; Check the cable connection. Check the pressur switch S208 (pos 39). Check solenoid brake valve "D211". (pos 38).Item no 131325 Check pressure reduction valve. (pos 32) Item no.131076 ; Check pressure control valve (pos 37) Item no 131071. Check Battery backup. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 190 | Pitch A ref:__._°, Act.:__._° | The difference between pitch and the actual pitch has been higher than the allowable limit. | Check; The plug connection to proportional valve Y800A. pos.82./ Defect proportional valve Y800A pos.82. Item no. 193415. / High friction in bearing. Check for loose connections and noise. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 191 | A Ctrl:___.__V P.Vel:___._°/s | The difference between expected pitch velocity and the actual pitch velocity has been higher than the allowable deviation. | Check for bad connections to the proportional valve. / Defect porportional valve. / High friction in pitch baring. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 192 | A CtrlV.STD _.___V MEAN__.___V | Check for bad connections to the proportional valve. / Defect porportional valve. / High friction in pitch baring. | Possible reasons : -fault in position tranducer (Balluf), -Controller is unstable., -Fault in (V)RCC (on turbines with RCC) |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 193 | PowerSTD____._kW MEAN____._kW
|  |  | 194 | Pitch too low: __._° < __._° | The Error is reported if the turbine is in stop mode "90,0°" and the actual measured pitch is less than 80,0°. | Check Balluf A800, A800A, A800B and A800C. Check cable for balluf. Check and adjust balluf. On V39-V47 check CT3220 pos X4 and CT3153 pos Y1. On V63, V66 and V80 check CT3220 pos X2. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 195 | PowerError ____._ kW | Reported if the filtered difference between measured turbine power and power reference gets too large. It is calculated as Power reference – Actual power. • If the log shows a negative power error, the actual power was higher than the reference. • If the log shows a positive power error, the actual power was lower than the reference. | Reasons:  Extreme wind conditions  Wrong regulation parameters  Changed stationary working points (Power / Speed)  Defective VRCC-unit * FLJ: 99,5%: Power electronics + CT257 / CT 273 (ABB) Corrective actions: 1. Take a VDF and Ram Dump. 2. Check if turbine is configured according to parameter wizard. 3. Inspect the Power Electronic Unit. 4. Check the Resistor Unit. 5. There are vdf-track examples for this error in the linked xls-file(s). 6. If “PowerError -75.1 kW“ or “PowerError 75.3 kW“ software is okay, but if there is an error message like “PowerError -3.6 kW“ or “PowerError 19.1 kW“ there is an internal parameter error which cannot see by checking parameters --> Upload / install software agian |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 196 | RCC CRC error | There is Communication problems between the VMP (Vestas Multi Processor) controller and the RCC (Rotor Current Control) The error occurs if the VMP can´t read the data from the RCC for a period of 5 seconds. | Reasons: * Defective VRCC controller CT273 * Defective VMP controller CT3514 / 5V supply CT3357 (The communication port of the CT3514 is supplied by the CT3357) * Poor connection between VRCC controller and VMP controller Corrective Actions: 1. Take a VDF and Ram Dump 2. Check if turbine is configured according to parameter wizard 3. Perform VRCC Communication Checks with VT190663. 4. Inspect the Power Electronic Unit. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 197 | RCC Timeout | There is communication problems between the VMP ("Vestas Multi Processor") controller and the RCC (" Rotor Current Controller"). The VMP controller have not recived data from the RCC for 5 seconds. | Reasons: * Defective VRCC controller CT273 * Defective VMP controller CT3514 / 5V supply CT3357 (The communication port of the CT3514 is supplied by the CT3357) * Poor connection between VRCC controller and VMP controller * FLJ: NEVER Power electronics Corrective Actions: 1. Take a VDF and Ram Dump 2. Check if turbine is configured according to parameter wizard 3. Perform VRCC Communication Checks with VT190663. 4. Inspect the Power Electronic Unit. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 198 | CRC/Timeout error to RCC | There is communication problems between the VMP ("Vestas Multi Processor") controller and the RCC (" Rotor Current Controller"). The VMP controller have not recived data from the RCC. in 5000 msec. | Reasons: * Defective VRCC controller CT273 * Defective VMP controller CT3514 / 5V supply CT3357 (The communication port of the CT3514 is supplied by the CT3357) * Poor connection between VRCC controller and VMP controller Corrective Actions: 1. Take a VDF and Ram Dump 2. Check if turbine is configured according to parameter wizard 3. Perform VRCC Communication Checks whit VT190663. 4. Inspect the Power Electronic Unit.
|  |  | 199 | RCC status error:______ | Log: RRC status error__________ Signal: RCC telegram (RCC + VRCC) Monitoring: PAUSE or RUN and communication with the RCC. The controller starts to communicate with the RCC when the generator RPM is above 1200 o/oo (P11,2) of nominal generator RPM and Bit 0 in (P9,7) is 1. Criteria: The VMP controller reports error if there is an status error in 5000msec. (P11,8). Reaction:Pause Acknowledgement: Auto short Category: Turbine | e.g. RCC status error: 136: 128 (RCC on) + fault bit in this case 8 (128 +8 = 136) temperature * FLJ: 99,5%: Power electronics + CT257 / CT 273 (ABB) |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 200 | RCC header error | The error is reported, by the VMP (Vestas Multi Control) controller if it receives a telegram from the RCC (Rotor Current Control) it has not ordered for 5 seconds. | Reasons: * Defective VRCC controller CT273 * Defective VMP controller CT3514 / 5V supply CT3357 (The communication port of the CT3514 is supplied by the CT3357) * Poor connection between VRCC controller and VMP controller Corrective Actions: 1. Take a VDF and Ram Dump 2. Check if turbine is configured according to parameter wizard 3. Perform VRCC Communication Checks with VT190663. 4. Inspect the Power Electronic Unit. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 201 | RCC IVCE error _ | Error signal generated by the IGBT driver in case of: * The voltage drop across the IGBT getting too high while it is conducting (switched on). * Over-temperature shut-down of the IGBT-driver * Under-voltage lockout of the IGBT-driver | Reasons: * Defective power electronic unit * Defective controller CT273 * See Error 298, 299, RCC Temperature Errors * See Error 300, 301, RCC Voltage Errors * FLJ: exchange Power electronics + CT257 / CT 273 (ABB) Corrective actions: 1.Take a VDF and Ram Dump. 2.Check if turbine is configured according to parameter wizard 3.Inspect the Power Electronic Unit. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 202 | RCC ILIM error _ | Reported if the instantaneous rotor current exceeds 130% of nominal current. As this is monitored by a comparator in the VRCC-controller, the I-LIM-trigger-level cannot be changed by any parameter. However, the rotor current to reset this error is set by parameter “A rms ILIM hysteresis” (Group 11) | Reasons:  Grid failure (Voltage dips, etc)  Regulation error  Defective power electronic unit  Defective controller  Defective thyristors in ground controller * FLJ: exchange Power electronics + CT257 / CT 273 (ABB) Corrective actions: 1. Take a VDF and Ram Dump. 2. Check if turbine is configured according to parameter wizard. 3. Inspect the Power Electronic Unit. 4. Check softstart thyristors. | (RCC ILIM error 1) 1. Transfomer 2. Bottom Panel Fuse 3. Capacitor insulation test |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve | 4 / 3.9 | 2 | Y | - | 1. 저풍속으로 인하여 수요일 발전 테스트 예정 | 2018.01.15 | 001 | #15
|  |  | 203 | RCC temperature error _ | The error is reported from the RCC ( Rotor Current Control) if the temperatur in the RCC unit reach it´s max temperatur limit, in more than 5 seconds. Normal this error is reported by Weier generator RCC if the temperature is to high in one of the systems. Error 1 : Over temperature in system 1. Error 2 : Over temperature in system 2. Error 3 : Over temperature in controller. | Check temperature in Generator and RCC/VRCC. * FLJ: exchange Power electronics + CT257 / CT 273 (ABB) |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 204 | RCC voltage error ___ | This error is reported by the RCC (Rotor Current Control) if the voltage is too low or too high in an internal supply. This error is logged by the VMP (Vestas Multi Processor) controller if the RCC has reported voltage error in 5000 msec. Error log. 1= -11 Volt for analogue measurement. 2 = 11 volt for analogue measurement. 3 = 15 votlt. | * FLJ: First measure Resistor --> If resistor okay: Power electronics + CT257 / CT 273 (ABB) Check the RCC control unit or the effektelektronic unit. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 205 | RCC RAM error | Internal system error; its reported by the RCC if the contents of the memory in the RCC is destroyed. | Check the Connection between the RCC and the controller. Check the RCC. Check the controller. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 210 | Low gear temp: _, ___°C | The error is generated if the gear oil temperature is below -5 degrees and not above -2 degrees, the turbine goes into pause until the temperature is higher than 5 degrees. | Check the PT100 sensor R402 and the circuit connection. On V39-V47 check CT3220 pos X1. On V63, V66 and V80 check CT3220 pos X7. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 212 | Error temp.sensor R___, ___°C | The error occure if a temperature sensor shows values higher than 205 degrees or -5 degrees. | Check connection to the PT100 and the PT100 wiring circuit. Check the PT100. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 214 | Low gear oil level | The gearbox is equipped with an oil level sensor "S404". If the oil level in the gearbox drops below a certain level an alarm is triggered. | Possible reasons: - low oil level in the gearbox "S404". -Oil is cold and tick, and is moved to one side of the gear during start-up. -Oil is foaming. -Float in level swicth is swelling. -Float in level switch is bloked by metal dust due to pollution or gear damage. -Electrical fault, bad wiring. -leakage in gear. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 215 | Press.drop hydr.filt.Hub ___°C | This is a Warning. The hydraulic oil filter in the hub is nearly blocked, and the pressure drop across the filter has disabled S215. | Change the hydraulic filter in hub. Check Hydraulic pressure drop switch in hub S215. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 216 | Oil leakage in Hub | The error is reported, if the leak oil reservoir in the hub has been filled with oil, and the oil level sensor has been activated. (S217). The reservoir receives leak oil from the pitch piston, and the bursting disc. | Check the bursting disc. pos.76 Hydr. overveiw drawing. Item no.109623. Check and clean the level switch "S217" pos 51. Hydr. overveiw drawing. Item no.109180. Check the pitch piston for leak. Check cabel connection for S217. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 217 | Thermoerror Int. Gen.Fan F___A | The thermorelay (F313A or F515A) for the internal generator fan, has detected a overload, on the fan motor, and the motor has been stopped (M544A). | Check the etxern generator fane motor for overload in high and low mode; Check/adjust the thermorealys Check the feedback from the thermorelay |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 218 | Thermoerror Int. Gen.Fan F___B | The thermorelay for the internal generator fan F544B, has detected a overload, on the fan motor, and the motor has been stopped | Check thermo relay F514 and F516. Check contactors K514 and K516. Check the fan F544B. Link to document: V63 and V66 AI: 924272 and AI: 924268. V80 AI: 927983 AI: 929210 |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 219 | Thermoerror Ext. Gen.Fan F___ | The thermorelay (F510 or F508) for the extern generator fan, has detected a overload, on the fan motor, and the motor has been stopped (M541). | Check the etxernal generator fane motor "M541" for overload in high and low mode; Check/adjust the thermorealy F510 or F508; Check the feedback from the thermorelay F510/F508 to CT3133. pos X4. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 220 | New SERVICE state: _ | This event is logged in the controller when you enter the service code on the controller or when you go out of service in the turbine controller. It indicate that there are technicians in the turbine.
|  |  | 224 | Pause | This event is logged in the controller when the turbine is manually set in to pause. It indicate that there are pepole in the turbine.
|  |  | 228 | SysState _.___ set to ______
|  |  | 229 | Parameter __.___ set to ______
|  |  | 231 | Restart not possible |  | Check warning or alarm log for other errors, because this error is normally caused by another error.
|  |  | 232 | Power up after System error
|  |  | 236 | Error ___ acknowledged manual. | This event is logged in the controller when an error is acknowledged manual.
|  |  | 237 | WATCHDOG was not trigged | The controller has been restarted by the watchdog, and the controller has no indication of why the system has stopped trigging the watchdog. | Reboot the controller. Check warning log and alarm log, this error often comes as a reaction to another fault. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 238 | Busbarvent._, Power: ____._kW | This event is logged every time the heat exchanger starts and stops in the ground controller.
|  |  | 248 | Generator _ in | This event is logged in the controller every time the generator connect.
|  |  | 249 | Generator _ out | This event is logged in the controller every time the generator disconnect.
|  |  | 265 | Wind:___._ m/s Gen:____._ RPM
|  |  | 269 | Pitchtest nr. __ | The controller has received a telegram with a report of Pitch test, the nr indicate which pitch test is running. | Look in Alarm Log and Warning Log.
|  |  | 270 | Nac.vent.0, nac/gear:___/___°C | This event is logged in the controller every time the fan on the oilcooler stops.
|  |  | 271 | Nac.vent.1, nac/gear:___/___°C | This event is logged every time the fan on the oilcooler changes to lowspeed.
|  |  | 272 | Nac.vent.2, nac/gear:___/___°C | This event is logged in the controller every time the fan on the oilcooler changes to highspeed. On V6X and up its mediumspeed.
|  |  | 276 | Start auto-outyawing CCW | The turbine has started Auto outyawing counter clock weise.
|  |  | 281 | Start manual yawing CCW | it is an event it is when a fitter is starting yawing CCW ore CW
|  |  | 284 | Stop auto-outyawing
|  |  | 287 | Start hydr. oilcooler:___°C
|  |  | 288 | Standby heating _, gen: ___°C | This event is logged when the standby heating on the generator starts and stops.
|  |  | 289 | Gearoilheater _, gear: ___°C
|  |  | 291 | Top cntrl. fan__, Temp:___°C | This event is logged when the fan in the top controller stops and starts.
|  |  | 296 | RCC CE overvoltage: ____ V | Reported if the DC bus voltage exceeds 1050V, as measured by the controller. (Group 11, V VCE max limit). | Reasons:  Defective resistor unit  Defective power electronic unit  Defective VRCC controller  Defective connection between controller and power electronic unit  Defective thyristors in ground controller * FLJ: exchange REsistor, Power electronics + CT257 / CT 273 (ABB) Corrective actions: 1. Take a VDF and Ram Dump. 2. Check if turbine is configured according to parameter wizard 3. Check the Resistor Unit. (see XLS-file: Error 296 RCC CE overvoltage___V.xls) 4. Inspect the Power Electronic Unit. | 1. Cotroller Voltage 측정 2. Fuse, Cable inspection 3. VRCC inspection | 1. VRCC Resistor Unit : 1ea | 1. Multimeter 2. Pliers 3. Spanner 4. Hand tools | 1. Harness 2. Lanyard 3. Helmet 4. Sleeve | 7 / 6.6 | 3 | Y | - | 1. 파손된 Resistor part 2개에 대한 수리 요청 예정 | 2018.01.15 | 001 | #14
|  |  | 297 | RCC OVP active: ____ V | Reported by the OVP print board if the current measured through the thyristor exceeds app.100A. The voltage level (measured across the IGBT-power terminals) for turning the thyristor on is 950V +/-50V. The VMP (Vestas Multi Controller) controller has recieved a telegram with a report of RCC OVP (over voltage protection) is active. | Reasons:  Grid error  Defective thyristor switch-on in the ground controller  Loosened screws in power electronic unit  Defective power electronic unit  Defective resistor unit  Defective generator  Defective VRCC controller * FLJ: VRCC, only: Power electronics + CT 273 (ABB) Corrective actions: 1. Take a VDF and Ram Dump. 2. Check if turbine is configured according to parameter wizard 3. Inspect the Power Electronic Unit. 4. Perform Mechanical Inspection. 5. Check the Resistor Unit. --> this error might be linked to error 296; RCC CE overvoltage: ___V (see also Error 297 RCC OVP aktiv ___V.htm) |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Insulation tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. Insulation gloves
|  |  | 298 | RCC high temperature _ | Reported if the temperature in the VRCC is too high for 5 seconds. 1.Not used (Only old versions: Diode) 2.IGBT 3.Controller | Reasons: * Hose for blow-off air has fallen off or is clogged. * Poor connection between controller and power electronic unit (only for failure 2; typically displayed as “117C”) * Defective power electronic unit * Defective VRCC controller * Reversed air-flow of VRCC-ventilator, especially after gear-box change, when the direction of generator rotation has changed. * FLJ: Generator bearings hot? --> Power electronics + CT257 / CT 273 (ABB) Corrective actions: 1. Take a VDF and Ram Dump. 2. Check if turbine is configured according to parameter wizard 3. Measure the Supply Voltage to the Controller. 4. Inspect the Power Electronic Unit. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Insulation tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. Insulation gloves
|  |  | 299 | RCC low temperature _ | Reported if the temperature in the VRCC is too low for 5 seconds. 1.Not used (Only old versions: Diode) 2.IGBT 3.Controller | Reasons: * Check ambient temperature. * Defective temperatur sensor. * Poor connection between controller and power electronic unit (only for failure 2; typically displayed as “117C”) * Defective power electronic unit * Defective VRCC controller * Reversed air-flow of VRCC-ventilator, especially after gear-box change, when the direction of generator rotation has changed. Corrective actions: 1. Take a VDF and Ram Dump. 2. Check if turbine is configured according to parameter wizard 3. Measure the Supply Voltage to the Controller. 4. Inspect the Power Electronic Unit. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Insulation tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. Insulation gloves
|  |  | 300 | RCC high voltage ___ | This error is reported by the Vestas RCC if the voltage in an internal supply is too high for 5 seconds. | Reasons: * Defective VRCC controller * Defective power electronic unit * Loose connections on 24V supply to CT273 * Failure caused by grid voltage dip * FLJ: Power electronics + CT 273 (ABB) Corrective actions: 1. Take a VDF and Ram Dump. 2. Check if turbine is configured according to parameter wizard 3. Measure the Supply Voltage to the Controller. 4. Inspect the Power Electronic Unit. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Insulation tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. Insulation gloves
|  |  | 301 | RCC low voltage ___ | The error is reported if the RCC (Rotor Current Control) reports low voltage in 5000 msec. This error is reported by the RCC unit, if the voltage in an internal supply is too low for 5 seconds. | Reasons: * Defective VRCC controller * Defective power electronic unit * Loose connections on 24V supply to CT273 * Failure caused by grid voltage dip * FLJ: Power electronics + CT 273 (ABB) Corrective actions: 1. Take a VDF and Ram Dump. 2. Check if turbine is configured according to parameter wizard 3. Measure the Supply Voltage to the Controller. 4. Inspect the Power Electronic Unit. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Insulation tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. Insulation gloves
|  |  | 305 | PComp. dis. step__.__/__.__Hz | Logged when the phase compensation is disconnected because of steps/cut in the grid, to avoid high voltage. The phase compensation is reconnected when the grid has been normal for 60 sec. | Check the grid. check that there are liqual power on all 3 phases. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. valves tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. Insulation gloves
|  |  | 311 | Trip Q8 Feedback error | If one of the contactores has feedback 1 ("positiv feedback error") which indicates a welded contactor, the Q8 is tripped in order to stop the motor controlled by this contactor. If the turbine after reaction to an feedback error still has an feedback 1, the Q8 is trippede after 30 sec. If the faulted contactor is K700/K705 then the delay is omly 1 sec. The name of offending contactor can be seen in the previous log message("picture 9. Alarm log. service menu") | The name of offending contactor can be seen in the previous log message("picture 9. Alarm log. service menu") Replace offending contactor. The controller can trip Q8 due to : -overvoltage. -overcurrent. -Feedback error, welded contactor. If a turbine has a tripped Q8, the grid voltage has to be checked before the breakers is closed, and controller is started. When the controller is started, it can be seen in the log if the controller has tripped the breaker! |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Insulation tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. Insulation gloves
|  |  | 312 | Thermo error, ventilators T53 | The error occure if one of the six ventilators for cooling of the high voltage transformer "T53" has been overloaded, and the termistor has disabled the feedback signal "F20" from the ventilators to the controller. | Check the cable connections from the ventilatores to the connection box A16; check the ventilatores; Check the signal from box A16 to the rack A1.X7; Check the CT3220. pos X7. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Module tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. Insulation gloves
|  |  | 313 | Ambient temperature high: __°C | The error is generatet if the ambient temperatur is higher than 40ºC. This error will autorestart after 60 sec. If the temp. sensor shows 205° deg. or -45° deg. the sensor is defekt, and need to be replaced. | Check; Ambient sensor R300; / Check cable connection W380 from sensor to the connections box A9. (con. Ø10, Ø11.) (V66); / Check cable connection W384 from connections box A9 to CT3220.(V66): / Check cable connection W380 from sensor to CT3220. (V47). |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Module tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 314 | Trip Q8 high current L_ ____ A | The error occures if the turbine still have high current on one of the phases after disconnecting the generator. The controller can trip Q8 due to : -Overvoltage; -Overcurrent; -Feedback error, or welded contactor. | If the turbine has tripped Q8, the grid voltage has to be checked before the breackers is closed, and controller is started. When the controller is started, it can be seen in the log why the conrtoller has tripped Q8. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 315 | ExEx low voltage L_: ___V | The error occures if the grid is cutoff to the turbine. | Unstable Grid. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 316 | Windvaneerror __._m/s __._° | The windvane is not moving at a windspeed, where the vane is expected to move. The error is loged if, the wind is above 4 m/s and the sensor has not moved 5° deg. within the last 120 sec. The error can occure if there is ice on the sensor, and the vane can´t move, or cab be due to an error in the sensor (A327), or the communication cable to the sensor (W382). | Check the windvane sensor (A327 V66) (B302 V47); / Check the cable connection (W382) between the wind vane and CT3218 (X1 V66) (X3 V47); / Check CT3218 (X1 V66) (X3 V47). |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 317 | Extreme yawerror __._m/s __._° | The extreme yaw error occurs if the windspeed are more than 15 m/s and the wind direction suddenly change more than 45 deg. This error will normally come, in areas where the turbine is placed on mountains, where wind suddenly changes very fast. It could be as well caused by an error in the yaw-sensor, or in the communication cable to the yaw-sensor. | Check / adjust yaw-sensor remember to on twist.; Check communication cable to the yaw-sensor. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Module tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 320 | Hot HV trafo ___°C ______kW | The power reference is reduced due to hot high voltage trafo. The downregulation starts when the ambient temperature is 5 ° from the ambient temperature alarm limit 40°, and the transformer temperature is 5 ° from the high transformer temperature alarm limit 150° |  |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner 5. Module tester | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 323 | Power Curve __._m/s ______kW | The difference between the meaured power and the measured wind is to high. The error occurs during cold weather, where there is a chance of over-iceing. The wind is corrected for mass, and converted to power by a power curve. If the measured power is above the calulated power ("power curve") the error is reported. If the measured power is below the calulated power ("power curve") the error is reported. | Check the wind-vane B302/B303 , and the anemometer B301. Check the cups on the anemometer, is recording to the parameters. examle M99, M98 or old vestas. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 324 | Lightning detected
|  |  | 326 | Lightn. det. emergency suppl. | This is an Warning. This error is generated, if the lightning detector is broken. | Check lightning detector S346.
|  |  | 330 | PitchA pos:__._° Vel:____._°/s | If the pitch position sensor supervision (Balluf) measured voltage is not inside the adjusted limet, + the tolerances, of the balluf endstop. An error message is given. Furthermore an error is given, if the position sensor has detected a pitch speed that is not mechanical possible. | Check the adjustment of the balluf. / Check for electrical noise. / Check for problems whit the signal transmission line between VMP ("Vestas Multi Processor") control system and the pitch sensor. There are vdf-track examples for this error in the linked xls-file(s). |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 331 | PitchB pos:__._° Vel:____._°/s | If the pitch position sensor supervision (Balluf) measured voltage is not inside the adjusted limet, + the tolerances, of the balluf endstop. An error message is given. Furthermore an error is given, if the position sensor has detected a pitch speed that is not mechanical possible. | Check the adjustment of the balluf. / Check for electrical noise. / Check for problems whit the signal transmission line between VMP ("Vestas Multi Processor") control system and the pitch sensor. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 332 | PitchC pos:__._° Vel:____._°/s | If the pitch position sensor supervision (Balluf) measured voltage is not inside the adjusted limet, + the tolerances, of the balluf endstop. An error message is given. Furthermore an error is given, if the position sensor has detected a pitch speed that is not mechanical possible. | Check the adjustment of the balluf. / Check for electrical noise. / Check for problems whit the signal transmission line between VMP ("Vestas Multi Processor") control system and the pitch sensor. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 335 | Thermistor fail oil conditio. | The error is reported, if the thermorelay "F411" to the oilconditioning system has been activated, and cut the power to the gearoil pump "M440". | Check the gearoil pump M440, for overload. / Check the thermorelay, and the cable connection to CT3133 pos. X4. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 336 | Pressure fail oil condition. | The oil-conditioning system cannot maintain the necessary pressure. | Check; Pressure from the gear oil pump, on pos 12.. 0,5 ±0,2 bar. / Gear oil pump. pos. 2. / adjust the Pressure switch, pos 9. 0,5 ±0,2 bar. Item no. 131028. / leak in the gear oil cooler systen.! only it the gear oil temp.Has been over 60° deg. There are suggestions at error 163 - VMP5000 |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve 5. Insulation gloves
|  |  | 339 | Invalid measurement US ID:__ | The ultrasonic windsensor sends invalid measurement results. | Check cable for US sensor. Check that the screen on the US cable is mounted. Check if there is mounted any ferrits on the cable. Check and measure power supply for US sensor. Check US sensor. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 340 | Timeout or Checksum US ID:__ | This error is generated if there are a communication error between the ultrasonic windsensor and the controller. | Check cable for US sensor. Check that the screen on the US cable is mounted. Check if there is mounted any ferrits on the cable. Check and measure power supply for US sensor. Check US sensor. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 342 | Max. Windspd acc._, ____m/s*s | The error is reported, if it is not possible that the windspeed has changed as fast as measured. | Check for noise in surroundings. Check cable for US/wind vane sensor. Check that the screen on the US/wind vane cable is mounted. Check if there is mounted any ferrits on the cable. Check and measure power supply for US/wind vane sensor. Check US sensor/wind vane. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 343 | Max. Winddir. speed ____°/s | A unrelistic change in windspeed has been measured, the windfane cannot move as fast as measured, and this error is generated. | Check for noise in surroundings. Check cable for US/wind vane sensor. Check that the screen on the US/wind vane cable is mounted. Check if there is mounted any ferrits on the cable. Check and measure power supply for US/wind vane sensor. Check US sensor/wind vane. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 345 | Emerg. Pitch A vel.:__._°/s | The balluf (The sensor that measure the pitch position) has measured a pitch-speed that is not realistic. This must be an error in the balluf. | Check the Balluf and the signal. Check for noise. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 346 | Emerg. Pitch B vel.:__._°/s | The balluf (The sensor that measure the pitch position) has measured a pitch-speed that is not realistic. This must be an error in the balluf. | Check the Balluf and the signal. Check for noise. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 347 | Emerg. Pitch C vel.:__._°/s | The balluf (The sensor that measure the pitch position) has measured a pitch-speed that is not realistic. This must be an error in the balluf. | Check the Balluf and the signal. Check for noise. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 353 | Thermoerror VRCC Pump F___
|  |  | 356 | Thermoerror SlipR fan F____ | Thermo error slipring fan, termister to Slipring fan has opened the curcuit. | Check the slipring fan. Check error is often that there is metal dust inside the fan so it breaks down. |  |  | 1. Multimeter 2. Driver | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 357 | High temp. slipring: ___°C
|  |  | 360 | Emerg.Pitch min:__._°max:__._° | There is a differens between the blades picth speed, when the emergency valves pitches the blades. | Check all accumulators. Check solenoid valves. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 361 | Anemom 2.err:__._m/s,____._RPM | Some turbines is mounted with two anemometer, one on the nacelle roof (anemometer 1.) and one on the tower (anemometer 2.) The error is logged from anemometer 2 , on the tower, due to a defect or an iced up anemometer. It is important that the error is corrected because the anemometer signal is part of a blade deflection reduction feature. | Check the tower anemometer B301B; Cable W381B and the plug to the anemometer, CT3218, pos X3. (V47 drawing.) |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 363 | Oil filter error | The error is genereted if the pressure drop across the oil filter has been to high. The supervision is only active when the oil temperature is above 40 deg. C. | Check the oil filter |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 364 | US error, turbine stopped | There is a error in the communication from the US "ultra sonic" windsensor sensor to the top controller. | Check for noise in surroundings. Check cable for US/wind vane sensor. Check that the screen on the US/wind vane cable is mounted. Check if there is mounted any ferrits on the cable. Check and measure power supply for US/wind vane sensor. Check US sensor/wind vane. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 365 | Missing VAMS permission _ |  | the turbine is missing ok signal for run from the SCADA system check com. to the turbine from the SCADA sustem and check the SCADA system is OK
|  |  | 370 | High Oscillation Transm. __m/s | Reported if the oscillations in the drive-train are higher than the alarm level. | Reasons:  Wrong parameters  Condition of gear torque arms  Extreme wind conditions  Broken VRCC-resistors  Generator failure Corrective actions: 1. Take a VDF and Ram Dump. 2. Check parameters, especially generator-parameters for VRCC-regulation 3. Check gear torque arms 4. Check generator according to SWI 959335 5. Inspect the Power Electronic Unit. 6. Check resistor unit. |  |  | 1. Multimeter 2. Driver 3. Grip tools 4. Spanner | 1. Helmet 2. Harness 3. Lanyard 4. Sleeve
|  |  | 371 | [Log 371, ______,______]
|  |  | 392 | [Log 392, ______,______]
|  |  | 999 | Missing information